MARLDEN PANEL PRODUCTS LTD

Line 2 VFD Upgrade — Controlled Record Set Reconciliation

Drawing set for pre-energisation verification pack BV-2026-L2-01 (Simone Beaufort, 08/21/2026)

| Project | PROJ-L2VFD-2026 — Line 2 MCC VFD Upgrade, Marlden Works, Dumfries |
| --- | --- |
| Gate served | Restart Criterion 3 (records match field), ahead of Criterion 1 (independent verification, 08/21/2026). The same drawing set goes to the Criterion 2 inspection pack (Idris Wachowski, Harrowgate, 08/26/2026). |
| Date | 08/07/2026 |
| Prepared for issue by | R. James, Lead Electrical Engineer |
| To | D. Okonkwo, Engineering Records / Document Control (holder of the controlled record set) D. Fenwick, Senior Maintenance Electrician (owner of the drawing re-issue queue) |
| Copy | C. Whitmore, Ravenscar Commissioning Services (RFI register owner; records pack with Document Control) · file |
| Contents | 1 Reconciliation, drawing by drawing 2 Covering note to Denise Okonkwo 3 File note — basis settled |

# 1  Reconciliation — drawing by drawing

## 1.1  The test applied

Three references decide each call.

Restart Criterion 3 (MPP-RC-L2-001 Rev A, §4). The controlled record set must match the as-installed condition of Line 2 before verification proceeds. Each approved RFI affecting a drawing is either incorporated at re-issue or presented with the still-issued drawing and its field markup, as QMS-STD-ENG-001 §5 requires. Every open RFI affecting Line 2 is closed before the verifier's visit. Superseded drawings are not relied on.

QMS-STD-ENG-001 Rev D, §3–§5. Every field change to an issued drawing needs a numbered, approved RFI. A field markup is red pen on a print of the current issued revision. A re-issue takes the next revision letter and cites the RFIs it incorporates. A revision letter is never used twice. Title-block status is one of four values: ISSUED FOR CONSTRUCTION, FOR APPROVAL, AS-BUILT or SUPERSEDED.

The Line 2 RFI register (Engineering/RFIs/Line2_RFI_log.xlsx, last updated 07/14/2026) is what each drawing answers to. The as-installed condition is taken from the isolation log, the IR test record (07/25/2026), the Drive Parameter Record, P. Nandwani's termination notes (07/11/2026) and the refiner drive export (08/06/2026).

Standards cited in this document: IEC 61800-3 — Adjustable speed electrical power drive systems — Part 3: EMC requirements and specific test methods; IEC 60364-5-52 — Low-voltage electrical installations — Part 5-52: Selection and erection of electrical equipment — Wiring systems; IEC 61439-1 — Low-voltage switchgear and controlgear assemblies — Part 1: General rules; IEC 60947-2 — Low-voltage switchgear and controlgear — Part 2: Circuit-breakers. Short forms are used after this point.

## 1.2  Calls at a glance

| # | Document — current issue | Call | Goes into Simone's pack as | What must happen first | Ready |
| --- | --- | --- | --- | --- | --- |
| 1 | MPP-L2-PWR-002 Rev C — Power Distribution Schematic ISSUED FOR CONSTRUCTION 06/26/2026 | Re-issue as Rev D (AS-BUILT) | Rev D. Rev C goes only as the superseded change record, filed with RFI-014. | Walk-down; reconciliation RFI approved; RFI-025 closed and screens corrected in the field; RFI-031 closed. | Check 08/14/2026 Issue 08/17/2026 |
| 2 | PWR-002 Rev C field as-built markup — P. Nandwani 07/09/2026, unchecked | Retire to the change record | Change record only, filed with RFI-014 and superseded Rev C. Not presented as the installed condition. | Close-out note on RFI-014 action 4. | Filed 08/17/2026 |
| 3 | MPP-L2-MCC-001 Rev B — MCC General Arrangement ISSUED FOR CONSTRUCTION 07/08/2026 | Re-issue as Rev C (AS-BUILT) | Rev C. | Rev B issue history confirmed; RFI-021 and RFI-029 dispositions; walk-down; reconciliation RFI; RFI-031 closed. | Check 08/14/2026 Issue 08/17/2026 |
| 4 | MPP-L2-CBL-001 Rev B — Cable Schedule ISSUED FOR CONSTRUCTION 07/08/2026 | Re-issue as Rev C (AS-BUILT) | Rev C. | Cable walk-down; refiner feeder sizing decided (re-cabled if 6 mm² is installed); RFI-022 and RFI-025 closed, screens corrected; RFI-017 disposition. | Check 08/14/2026 Issue 08/17/2026 |
| 5 | MPP-L2-DEV-001 Rev B — MCC Device List 07/12/2026, “AS-BUILT — issued for verification pack” | Re-issue as Rev C (AS-BUILT) | Rev C. Rev B does not go in, whatever its status line says. | MCC walk-down recording the drive frame and serial at each position; reconciliation RFI; RFI-021 disposition; RFI-031 closed. | Check 08/13/2026 Issue 08/17/2026 |

In short: none of the five goes into Simone's pack on its current issue. Four controlled drawings go into Dougie's re-issue queue and come back as AS-BUILT re-issues. They are checked by close of 08/14/2026 and issued by Document Control on 08/17/2026, before pre-verifier prep starts on 08/18/2026. The field markup is retired to the change record. The same set goes into the Harrowgate inspection pack. Idris Wachowski needs that pack at least three working days before 08/26/2026, so by 08/20/2026. His booking asks for the latest controlled schematic matching the as-built configuration (item 1) and the as-built device list with coordinating fuse fitment (item 2).

Action references (A1–A20) are to the schedule in 1.11.

## 1.3  Drawing 1 — MPP-L2-PWR-002 Rev C, Line 2 Power Distribution Schematic

| Call | Re-issue as Rev D, status AS-BUILT. |
| --- | --- |
| Into Simone's pack as | Rev D. Rev C goes only as superseded, filed with RFI-014 and the 07/09/2026 markup for traceability. |
| Ready | Drafted 08/13/2026 (D. Fenwick) · checked 08/14/2026 (R. James) · issued 08/17/2026 (D. Okonkwo). |

### What it answers to in the register

| RFI | Register status | Bearing on PWR-002 | Position at 08/07/2026 |
| --- | --- | --- | --- |
| RFI-014 | Closed — Approved 07/08/2026 | Refiner drive feed moved from Section B to Section C, position C3, with an 80 A aR coordinating fuse. RFI-014 instructs re-issue as Rev D. | Not incorporated. Rev D has been pending since 07/08/2026 (RFI-014 action 4). |
| RFI-015 | Closed — Approved 07/03/2026 | aR semiconductor coordinating fuse on drive feeders. | Not shown on Rev C (approved after its issue). Rev D to show it. |
| RFI-025 | Open | Note 5 requires screened cable with 360° EMC glands. | Field departs from note 5 (single-end screen bonding). RFI to be closed and the field corrected to the note. |
| RFI-031 | Pending — vendor | External EMC filters for Section C drives would sit in the drive power path if fitted. | Open. Must be closed; drawn on Rev D if equipment is added. |

### Field against drawing

Feed. The refiner drive is fed from Section C, position C3. This is confirmed by RFI-014, DEV-001 Rev B note 2, isolation log ISO-2041, and the drive serial DTX60-2026-04477 in the 08/06/2026 export. Rev C note 4 and the diagram still show Section B via a 400 A MCCB.

Refiner circuit devices not on Rev C: input isolator QF-C3-00 (MG-SD160), coordinating fuse F-C3-01 (Bramble Fuseworks BFW-80aR, 80 A aR), drive frame DTX-60, output dV/dt filter FL-C3-01. DTX-60 is the correct heavy-duty frame for 44 A at 380 V (50 A HD), and 80 A aR is its specified fuse (DTX-DS-2025-06 §1.1, §4).

Circuits installed but not drawn. Rev C shows five drive circuits, but eleven drives are installed (Drive Parameter Record; IR test record). Rev C does not show:
• the infeed conveyor, outfeed conveyor, stacker, hydraulics pump, press-hood blower and dust-extract drives;
• the compressor and cooling-pump DOL circuits;
• the refiner preheaters H1/H2 (B2 on the GA and device list).
Rev C's “AUX HTG 63 A” in Section A appears on no other drawing. See 1.9.

Motor numbering. M6 is an auxiliary drive on Rev C but the compressor in the IR record. Rev D is to use the register motor tags (L2-M-…), which DEV-001 already names as canonical.

Cross-references. Rev C cites MPP-L2-MCC-001 “Rev B”. That letter appears to have been used twice (see 1.5). Rev D is to cite MCC-001 Rev C, CBL-001 Rev C and DEV-001 Rev C.

Change record. Isolation log ISO-2030 (07/04/2026) records the Section B recable “per RFI-014”. That is four days before RFI-014 was raised and approved (07/08/2026). RFI-014 also sits out of date order in the register (RFI-013 is dated 06/28/2026, RFI-015 07/01/2026). Simone's Item 1 cross-checks the RFI record against the field, so the conflict must be explained on the record before the pack goes.

### Not in the queue

Refiner motor replacement (C. Whitmore, e-mail 08/06/2026). This is not an approved change, so Rev D shows the motor that is installed: Bramwell BEM-180L-4A, 22 kW, 42 A at 400 V. If a replacement is approved, it comes through its own RFI and PWR-002 is revised again.

One point before any order is placed. The drive's own export at 10:21 on 08/06/2026 still holds the factory-template motor data (P1.01 30.0 kW, P1.02 58.0 A), and the two stationary tunes that aborted with F.203 ran against it. The e-mail says the nameplate values were entered the day before. Neither the export nor the DriveTec support log bears that out (the log records that the refiner was not started on 08/05/2026).

### What has to happen first — who — by when

| Ref | What | Who | By |
| --- | --- | --- | --- |
| A1 | Close RFI-025 in writing: VFD motor-cable screens are bonded 360° at both ends through KCC-EMC glands, with no pigtails (IEC 61800-3 extract §3; DTX-IOM-2025-04 §3.2, §4.1). Note 5 is right; the field is corrected to it (A12). | R. James | 08/10/2026 |
| A6 | MCC walk-down, Sections A–C: every position, functional unit and device, with drive model and serial. Signed sheet. Cubicle access under permit and isolation, with the VFD addendum steps logged. | D. Fenwick | 08/11/2026 |
| A10 | Reconciliation RFI raised, itemised from the walk-downs / approved. | D. Fenwick / R. James | 08/11/2026 / 08/12/2026 |
| A11 | RFI-031 closed in writing (DriveTec response obtained by C. Whitmore, A5). | R. James | 08/12/2026 |
| A14 | Draft Rev D: • refiner circuit from C3: QF-C3-00 → F-C3-01 BFW-80aR → DTX-60 → FL-C3-01 → screened cable → L2-M-REF-01; • every installed Line 2 circuit, with register motor tags; • revision note citing RFI-014 and the reconciliation RFI. | D. Fenwick | 08/13/2026 |
| A15 | Check Rev D. | R. James | 08/14/2026 |
| A16 | Annotate the RFI-014 record to explain the ISO-2030 date. | R. James | 08/14/2026 |
| A20 | Issue Rev D; stamp Rev C SUPERSEDED; close RFI-014 action 4. | D. Okonkwo | 08/17/2026 |

## 1.4  Drawing 2 — PWR-002 Rev C field as-built markup (P. Nandwani, 07/09/2026)

| Call | Retire to the change record. It is not re-drawn, and it is not presented as the record of the installed condition. |
| --- | --- |
| Into Simone's pack as | Change record only: filed with RFI-014 and superseded Rev C, stamped SUPERSEDED. BV-2026-L2-01 lists the markup, so Simone can see it there. |
| Ready | Filed by D. Okonkwo on 08/17/2026, when Rev D issues. |

What it answers to: RFI-014 only. It is the field capture called for by RFI-014 action 3. It cannot serve as the QMS §4 markup for RFI-014, for five reasons:

The black linework is not Rev C. It shows the incomer as “ACB-01 2500 A Icu 25 kA”. Rev C and DEV-001 have Q0-MAIN, an MG-SD2500 switch-disconnector, Icw 25 kA/1s. It also draws the press on Section C and the sander and conveyor on Section B. Rev C, the GA and the device list put the press at B3, the sander at C4 and the conveyor at C5, and isolation entries ISO-2032 and ISO-2037 agree. QMS §4 requires a markup on a print of the current issued revision.

The fuse is described as “Bussmann-style aR”. The fitted fuse is Bramble Fuseworks BFW-80aR (RFI-014; DEV-001 F-C3-01; stores STK-FUS-0088). The DTX conditional Icc rests on the specified fuse (DTX-DS-2025-06 §3–§4), and that is exactly what Simone's Item 2 checks.

It omits QF-C3-00 and FL-C3-01 on the refiner circuit.

It cites the wrong schedule revision: “Line 2 Cable Schedule — Rev D pending”. The schedule is at Rev B.

It is unchecked (the Chk field is “—”).

| Ref | What | Who | By |
| --- | --- | --- | --- |
| A20 | Record on the RFI-014 close-out that: • Rev D was prepared from the 08/10–08/11/2026 walk-down, not from the markup; • the markup's base linework and fuse description are superseded. File the markup with superseded Rev C and RFI-014. | D. Okonkwo (wording from R. James) | 08/17/2026 |

## 1.5  Drawing 3 — MPP-L2-MCC-001 Rev B, Line 2 MCC General Arrangement

| Call | Re-issue as Rev C, status AS-BUILT. |
| --- | --- |
| Into Simone's pack as | Rev C. The GA is not on BV-2026-L2-01's list of documents relied upon. It goes in anyway: it is a controlled drawing covering Line 2, Criterion 3 covers all of them, and the permit and method statement both work from it. |
| Ready | Drafted 08/13/2026 · checked 08/14/2026 · issued 08/17/2026. |

### What it answers to in the register

| RFI | Register status | Bearing on MCC-001 | Position at 08/07/2026 |
| --- | --- | --- | --- |
| RFI-014 | Closed — Approved 07/08/2026 | Refiner drive at C3 (note 3). | Incorporated. Rev B's revision note does not cite it, which QMS §4 requires. |
| RFI-021 | Closed — Approved 07/11/2026 | Section C cubicle ventilation; cites the “cubicle GA”. | Approved after Rev B was issued. The disposition is not on the register. |
| RFI-029 | Closed — Approved 07/14/2026 | Cubicle labelling (note 11). | Approved after Rev B was issued. The disposition is not on the register. |
| RFI-031 | Pending — vendor | EMC filter placement: inside the cubicle or in an adjacent panel. Cites the “cubicle GA”. | Open. |
| RFI-002, -006, -007, -010, -011 | Closed — Approved before 07/08/2026 | Tray reuse, gland plates, busbar rating, earthing, cut-outs. | No outstanding drawing effect found in the register text. Confirm against the dispositions. |

### Field against drawing

Drive positions. The position register shows four drive positions (B3, C3, C4, C5), but eleven drives are installed. Where the field and the GA disagree:
• ISO-2040 isolated at “MCC Section C position C6 upstream isolator” for the refiner aux-fan drive. The GA shows C6 as the cable-gland plinth.
• ISO-2043 isolated at “position C7” for the infeed-conveyor drive. The GA has no C7.
• CBL-001 has B5 (compressor) and B6 (stacker). The GA's Section B stops at B4.
• The blower and dust-extract drives appear only on the cable schedule (Section C, no position); the outfeed-conveyor and hydraulics drives appear on no drawing.

Section A functions and positions differ between the GA, the device list and the cable schedule. For example, the GA shows A5 as “spare — blanked”, the cable schedule feeds field instruments from A5 (A5-INST-01), and the device list puts the lighting and control-transformer MCBs at A1.

Revision letter. The GA's own history puts Rev A at 05/12/2026 (for tender) and Rev B at 07/08/2026. Yet documents dated before 07/08/2026 already cite “Rev B”:
• the archived pre-upgrade schedule MPP-L2-MCC-000 Rev G (06/01/2026: “superseded by MPP-L2-MCC-001 Rev B”);
• RFI-002 (06/04/2026);
• PWR-002 Rev C (06/26/2026).
Either an earlier Rev B was issued and the letter was used again on 07/08/2026, or documents were changed after issue. Both breach QMS §4. Either way the re-issue takes Rev C, and any earlier “Rev B” print is withdrawn and stamped.

### What has to happen first — who — by when

| Ref | What | Who | By |
| --- | --- | --- | --- |
| A3 | Confirm from the register what was issued as MCC-001 Rev B and when; locate any earlier prints. | D. Okonkwo | 08/10/2026 |
| A2 | Send the written dispositions of RFI-021 and RFI-029 to D. Fenwick. | D. Okonkwo | 08/10/2026 |
| A6 / A10 | MCC walk-down; reconciliation RFI raised and approved. | D. Fenwick / R. James | 08/11/2026 / 08/12/2026 |
| A11 | Close RFI-031. | R. James | 08/12/2026 |
| A14 | Draft Rev C: • complete position register for Sections A–C as installed (function, drive model, isolator, fuse), with C6 and C7 corrected; • ventilation, labelling and EMC filter location as RFI-021, RFI-029 and RFI-031 are dispositioned; • revision note citing RFI-014, the reconciliation RFI and whichever of RFI-021/-029/-031 change it; • cross-references to PWR-002 Rev D, CBL-001 Rev C and DEV-001 Rev C. | D. Fenwick | 08/13/2026 |
| A15 | Check Rev C. | R. James | 08/14/2026 |
| A20 | Issue Rev C; stamp every Rev B print SUPERSEDED. | D. Okonkwo | 08/17/2026 |

## 1.6  Drawing 4 — MPP-L2-CBL-001 Rev B, Line 2 Cable Schedule

| Call | Re-issue as Rev C, status AS-BUILT, once the field items below are closed. |
| --- | --- |
| Into Simone's pack as | Rev C. |
| Ready | Drafted 08/14/2026 · checked 08/14/2026 · issued 08/17/2026. |

### What it answers to in the register

| RFI | Register status | Bearing on CBL-001 | Position at 08/07/2026 |
| --- | --- | --- | --- |
| RFI-014 | Closed — Approved 07/08/2026 | Feed origin at C3, plus the coordinating-fuse reference (RFI-014 §3, first bullet). | Origin incorporated; fuse reference not. Action 5 is marked “Complete”. |
| RFI-017 | Closed — Approved 07/02/2026 | Supplementary tray run for screened VFD cables; cites the cable schedule. | Not reflected in Rev B. The disposition is not on the register. |
| RFI-022 | Pending — vendor | Refiner motor cable is installed about 6 m longer than scheduled (C3-REF-02: 18 m). | Open. |
| RFI-025 | Open | Note 2 states both-ends 360° glands. | The field is single-end. RFI to be closed and the field corrected to note 2. |
| RFI-013, -020 | Closed — Approved | Segregation; core marking (site standards). | No outstanding effect found. |

### Field against schedule

Unverified by its own account. Rev B describes itself as “updated per RFI-014; other rows carried forward from pre-upgrade schedule pending verification”. On its own statement it is not an as-built record.

Missing and wrong circuits. There are no rows for the sander (C4), refiner aux fan (C6), outfeed conveyor or hydraulics pump. C7 is shown as “spare drive feed — terminated, capped”, but it feeds the infeed-conveyor drive (ISO-2043). The blower and dust-extract rows carry legacy “C3-” tags, with their positions not reconciled (note 11). Checklist item 2 (signed 07/12/2026) records the terminations as checked “against the Line 2 Cable Schedule”, yet several installed circuits have no row to check against.

Refiner feeder sizing (project plan risk R2, due to be closed out before 07/25/2026). C3-REF-01 and C3-REF-02 are scheduled at 6 mm² for Ib 45 A. MPP-STD-SUM-05 gives Cg 0.80 (drive cubicles grouped in Section C) and Ca 0.87 (45 °C MCC room, 90 °C XLPE), so the required tabulated capacity is 45 / (0.80 × 0.87) = 64.7 A.
• 6 mm² is 49 A (Iz 34.1 A): it fails.
• 10 mm² is 66 A (Iz 45.9 A): the minimum on this basis. A larger size is needed if the walk-down finds more than six circuits sharing the run.
The other feeders scheduled at 4 mm² and above pass on the same factors. The removed-cable specification records the pre-upgrade refiner feeder as 10 mm², so the installed size has to be confirmed in the field. If 6 mm² is installed, R2 requires the feeder to be re-cabled before energisation, under its own RFI.

Screen termination. Note 2 states both-ends 360° glands, which is what IEC 61800-3 and DTX-IOM-2025-04 §3.2 require. P. Nandwani's notes (07/11/2026) record single-end pigtail bonding, with the motor-end screen left unbonded, on every VFD motor cable terminated: about ten at that date, and the rest to the same method. RFI-025 is open and checklist item 3 is unsigned. The field is corrected to the schedule, not the other way round. The KCC-EMC glands in stores (Rack 09-B, 07/12/2026 extract: 24 × M25, 18 × M32, 8 × M40) cover the job.

Construction. Rev B's type column says “4-core … screened/symmetrical”, but its size column says “3c × … + E”. The walk-down records the actual construction against DTX-IOM-2025-04 §3.1, which requires motor cable that is both screened and symmetrical.

### Not in the queue

Sander cable re-pull (D. Fenwick, note 08/06/2026). The IR row for IR-L2-SND-04 records “conductors not disturbed”. On the other twelve rows the drive-output conductors were disconnected. The readings also point the same way: phase–earth still rising through the 60 s, and 0.02 MΩ phase–phase. Together they fit a test into the drive output or its FL-C4-01 filter, not a damaged cable.

So the first step is a re-test with the output conductors disconnected, per DTX-IOM-2025-04 §6.1, and DriveTec's view on DR-L2-SND-01 (§6.1, §6.3). A re-pull is raised as an RFI only if the proper re-test fails. If one is raised, the cable must be screened symmetrical VFD cable with KCC-EMC glands at both ends, and the circuit gets a row on CBL-001. The recovered stock in Rack 12-A must not be used: STK-CBL-0044 and -0045 are unscreened, and IEC 61800-3 does not allow unscreened cable on a drive output.

### What has to happen first — who — by when

| Ref | What | Who | By |
| --- | --- | --- | --- |
| A4 | Confirm the installed CSA on C3-REF-01/-02; send the R2 derating calculation to R. James. | D. Fenwick | 08/10/2026 |
| A2 | Send the RFI-017 disposition to D. Fenwick. | D. Okonkwo | 08/10/2026 |
| A7 | Cable walk-down of every Line 2 outgoing circuit: tag by physical position, construction, CSA, measured route length, and gland and screen termination at both ends. Signed sheet. | P. Nandwani | 08/11/2026 |
| A8 | Re-test the sander circuit per DTX-IOM-2025-04 §6.1, before any re-pull decision. | P. Nandwani | 08/11/2026 |
| A9 | Decide the refiner feeder; if a re-cable is needed, approve its RFI (raised by D. Fenwick). | R. James | 08/11/2026 |
| A11 | Close RFI-022 in writing (DriveTec response via C. Whitmore, A5). A re-cabled output, cut to the measured route length, closes it. | R. James | 08/12/2026 |
| A12 | RFI-025 rework: motor-end screens re-terminated 360° through KCC-EMC glands; pigtails removed; earth continuity re-checked; checklist item 3 signed. Done under permit (C. Bretherton) and isolation (M. Odigie), with the VFD addendum steps logged. | P. Nandwani | 08/13/2026 |
| A13 | If required, re-cable the refiner feeder: input in 10 mm² XLPE/SWA minimum; output in screened symmetrical 10 mm² minimum, cut to route length; IR, continuity and torque records. | D. Fenwick / P. Nandwani | 08/13/2026 |
| A14 | Draft Rev C: • every installed circuit, tagged by physical position; • aR fuse per drive feeder (RFI-014); • measured lengths; • Cg, Ca and Iz against Ib on each row; • gland and screen termination; • revision note citing RFI-014, -017, -022, -025, the reconciliation RFI and the refiner feeder RFI. | D. Fenwick | 08/14/2026 |
| A15 | Check Rev C. | R. James | 08/14/2026 |
| A20 | Issue Rev C; stamp Rev B SUPERSEDED. | D. Okonkwo | 08/17/2026 |

## 1.7  Drawing 5 — MPP-L2-DEV-001 Rev B, Line 2 MCC Device List

| Call | Re-issue as Rev C, status AS-BUILT. |
| --- | --- |
| Into Simone's pack as | Rev C. Rev B does not go in, even though its status line says “issued for verification pack”. |
| Ready | Drafted 08/12/2026 (first in the queue) · checked 08/13/2026 · issued 08/17/2026. |

### What it answers to in the register

| RFI | Register status | Bearing on DEV-001 | Position at 08/07/2026 |
| --- | --- | --- | --- |
| RFI-014 | Closed — Approved 07/08/2026 | F-C3-01 BFW-80aR at C3. | Incorporated (note 2). |
| RFI-015 | Closed — Approved 07/03/2026 | aR class coordinating fuses. | Incorporated. |
| RFI-021 | Closed — Approved 07/11/2026 | Cubicle ventilation: any fans added or changed are devices. | The disposition is not on the register. |
| RFI-031 | Pending — vendor | External EMC filters would be devices if fitted. | Open. |

### Field against list

Item 2 of BV-2026-L2-01 tests whether the “device list matches installed devices in Section C”. Rev B lists three Section C drive units (C3, C4, C5). The C6 (refiner aux fan) and C7 (infeed conveyor) drive units, with their isolators and coordinating fuses, are installed and not listed. Five more drives (outfeed conveyor, stacker, hydraulics, blower, dust extract) are not on the list at all.

C5 has no isolator row, yet ISO-2037 isolated at the “C5 upstream isolator”, and note 4 says every Section C unit has one.

The fitted drive frame is not recorded at each position. The fuse rows identify the frame “per DTX Series datasheet §4”, which infers the frame from the fuse. At C3 the frame is confirmed independently (DTX-60, serial DTX60-2026-04477), and 80 A aR is its specified fuse. Every other position needs its frame recorded so the fuse match can be shown, as the IEC 61439-1 / IEC 60947-2 extract §3(c) requires.

Section incomers are missing. The schematic shows Section A/B/C MCCBs (250 A, 400 A, 400 A), and the isolation log isolates at section incomers at A1, B1 and C1. None of them is on the device list.

Unmatched local fan. Q-LOC-AUX-01 / K-LOC-AUX-01 (2.2 kW local fan) match no motor on the Line 2 motor register. Confirm or remove.

Format. The status line is not one of the four permitted values (QMS §3), and there is no revision history citing RFIs (QMS §4).

### What has to happen first — who — by when

| Ref | What | Who | By |
| --- | --- | --- | --- |
| A6 | MCC walk-down, including drive model and serial at each position (as for Drawing 1). | D. Fenwick | 08/11/2026 |
| A10 | Approve the reconciliation RFI. | R. James | 08/12/2026 |
| A2 / A11 | RFI-021 disposition (D. Okonkwo, 08/10/2026) and RFI-031 closure (R. James, 08/12/2026). Any devices either adds go on Rev C. | as stated | 08/12/2026 |
| A14 | Draft Rev C: • every installed device in Sections A–C, including the section incomers; • drive model, frame and serial at each position; • isolator and aR fuse for each drive unit, and the filters; • position crosswalk to the register motor tags; • status AS-BUILT, with a revision history citing RFI-014, RFI-015, the reconciliation RFI and any of RFI-021/-031. | D. Fenwick | 08/12/2026 |
| A15 | Check Rev C. | R. James | 08/13/2026 |
| A20 | Issue Rev C; stamp Rev B SUPERSEDED. | D. Okonkwo | 08/17/2026 |

## 1.8  Dougie's re-issue queue

| # | Drawing | From → to | Incorporates | Draft | Check | Issue |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | MPP-L2-DEV-001 Device List | Rev B → Rev C, AS-BUILT | RFI-014, RFI-015, reconciliation RFI; RFI-021 and RFI-031 if they add devices | 08/12/2026 | 08/13/2026 | 08/17/2026 |
| 2 | MPP-L2-PWR-002 Power Distribution Schematic | Rev C → Rev D, AS-BUILT | RFI-014, reconciliation RFI; RFI-031 if it is in the power path | 08/13/2026 | 08/14/2026 | 08/17/2026 |
| 3 | MPP-L2-MCC-001 MCC General Arrangement | Rev B → Rev C, AS-BUILT | RFI-014 (now cited), reconciliation RFI; RFI-021, -029 and -031 as dispositioned | 08/13/2026 | 08/14/2026 | 08/17/2026 |
| 4 | MPP-L2-CBL-001 Cable Schedule | Rev B → Rev C, AS-BUILT | RFI-014 (fuse reference), RFI-017, -022, -025, reconciliation RFI, refiner feeder RFI if raised | 08/14/2026 | 08/14/2026 | 08/17/2026 |

Prepared by D. Fenwick and checked by R. James on every re-issue (QMS §3: prepared and checked are different people). Each title block cites the RFIs incorporated. Not in the queue:
• the 07/09/2026 markup, which is retired;
• the refiner motor replacement;
• the sander cable re-pull.
If either of the last two is approved, it comes through its own RFI and re-enters the queue.

## 1.9  Position cross-check — what each drawing shows against the field

Eleven drive-fed motors and two DOL motors are installed: the 13 Line 2 motors on the motor register and in the IR record. The GA and device list show four drives, the schematic five, and the cable schedule six — and not the same six.

| Circuit (motor / drive) | PWR-002 Rev C | MCC-001 Rev B | DEV-001 Rev B | CBL-001 Rev B | Field evidence |
| --- | --- | --- | --- | --- | --- |
| Refiner L2-M-REF-01 / DR-L2-REF-01 (DTX-60) | Section B (superseded by RFI-014) | C3 | C3: QF-C3-00, F-C3-01 BFW-80aR, FL-C3-01 | C3-REF-01/-02 (6 mm²) | ISO-2041 at C3; export serial DTX60-2026-04477 |
| Refiner aux fan L2-M-REF-02 / DR-L2-REF-AUX-01 | “M6 AUX”, Section C (presumed) | — (C6 shown as gland plinth) | — | — | ISO-2040: C6 upstream isolator; IR-L2-AUX-02 |
| Press L2-M-PRS-01 / DR-L2-PRS-FEED-01 (DTX-45) | Section B | B3 | B3: QF-B3-00, F-B3-01 63 A aR | B3-PRS-01/-02 | ISO-2032 at B3; IR-L2-PRS-03 (markup draws it on Section C) |
| Sander L2-M-SND-01 / DR-L2-SND-01 | Section C | C4 | C4: QF-C4-00, F-C4-01, FL-C4-01 | — no row — | IR-L2-SND-04 FAIL (markup draws it on Section B) |
| Main conveyor L2-M-CNV-01 / DR-L2-CNV-MAIN-01 (DTX-45) | Section C | C5 | C5: F-C5-01 only — no isolator row | C5-CNV-01/-02 | ISO-2037: C5 upstream isolator (markup draws it on Section B) |
| Infeed conveyor L2-M-INF-01 / DR-L2-CNV-IN-01 | — | — (no C7) | — | C7-SPR-01 “spare, capped” | ISO-2043: C7 upstream isolator; IR-L2-INF-09 |
| Outfeed conveyor L2-M-OUT-01 / DR-L2-CNV-OUT-01 | — | — | — | — | IR-L2-OUT-10; Drive Parameter Record |
| Stacker L2-M-STK-01 / DR-L2-STK-01 | — | — (no B6) | — | B6-STK-01 | IR-L2-STK-11 |
| Hydraulics L2-M-HYD-01 / DR-L2-HYD-PMP-01 | — | — | — | — | IR-L2-HYD-12 |
| Press-hood blower L2-M-BLW-01 / DR-L2-BLW-01 | — | — | — | C3-BLW-01/-02 (legacy tag; position not reconciled) | IR-L2-BLW-13 |
| Dust extract L2-M-DEX-01 / DR-L2-DST-EXT-01 | — | — | — | C3-DUS-01/-02 (legacy tag; position not reconciled) | IR-L2-EXT-07 |
| Compressor L2-M-CMP-01 (DOL) | — | — (no B5) | — | B5-CMP-01 | ISO-2038 local isolator; IR-L2-CMP-06 |
| Cooling pump L2-M-CLP-01 (DOL) | — | B4 | — | B4-COOL-01 | ISO-2042 local isolator; IR-L2-CPM-08 |
| Refiner preheaters H1/H2 | — | B2 | B2: Q-B2-01/-02 | — | — |
| MCC-room aux heating 63 A | Section A “AUX HTG” | — | — | — | — |

## 1.10  RFI register — what must be closed before the set is checked

Close in writing (these change drawings): RFI-025 (R. James, 08/10/2026); RFI-022 and RFI-031 (DriveTec responses obtained by C. Whitmore by 08/11/2026; closed by R. James by 08/12/2026).

Retrieve the dispositions of three approved RFIs whose effect on the drawings the register does not record: RFI-017, RFI-021 and RFI-029 (D. Okonkwo, 08/10/2026).

Incorporate RFI-014 into PWR-002 Rev D and CBL-001 Rev C, and explain the ISO-2030 date on the RFI-014 record (R. James, 08/14/2026).

Raise, at the next free numbers:
• the as-built reconciliation RFI (D. Fenwick 08/11/2026; R. James approves 08/12/2026);
• if 6 mm² is installed, the refiner feeder re-cable RFI (08/11/2026).

Close for Criterion 3, although they change none of these drawings:
• RFI-023 and RFI-032 (D. Okonkwo);
• RFI-024, -027, -030, -033 and -034 (R. James);
• RFI-028 (DriveTec / R. James).
RFI-027 and RFI-034 bear on control and PLC drawings, which are not in this set.

The register copy in Engineering/RFIs is dated 07/14/2026 and shows eleven items open or pending. C. Whitmore, as register owner, issues a current copy to D. Okonkwo by 08/14/2026 with the new RFIs entered.

## 1.11  Action schedule by date

| Ref | Action | Who | By |
| --- | --- | --- | --- |
| A1 | Close RFI-025 in writing: 360° screen bonding at both ends through KCC-EMC glands, no pigtails | R. James | 08/10/2026 |
| A2 | Send the written dispositions of RFI-017, RFI-021 and RFI-029 to D. Fenwick | D. Okonkwo | 08/10/2026 |
| A3 | Establish what was issued as MPP-L2-MCC-001 Rev B and when; locate earlier prints | D. Okonkwo | 08/10/2026 |
| A4 | Confirm the refiner feeder's installed CSA; send the R2 derating calculation to R. James | D. Fenwick | 08/10/2026 |
| A5 | Obtain DriveTec's written responses to RFI-022 and RFI-031; obtain DriveTec's view on DR-L2-SND-01 | C. Whitmore | 08/11/2026 |
| A6 | MCC walk-down, Sections A–C: positions, devices, drive model and serial. Signed sheet (cubicle access under permit and isolation) | D. Fenwick | 08/11/2026 |
| A7 | Cable walk-down of every outgoing circuit: construction, CSA, length, glands and screen termination. Signed sheet | P. Nandwani | 08/11/2026 |
| A8 | Sander IR re-test with the drive-output conductors disconnected (DTX-IOM-2025-04 §6.1) | P. Nandwani | 08/11/2026 |
| A9 | Decide the refiner feeder; approve the re-cable RFI if needed | R. James | 08/11/2026 |
| A10 | Reconciliation RFI raised / approved | D. Fenwick / R. James | 08/11/2026 / 08/12/2026 |
| A11 | Close RFI-022 and RFI-031 in writing | R. James | 08/12/2026 |
| A12 | Re-terminate motor-end screens; remove pigtails; sign checklist item 3 (permit: C. Bretherton; isolation: M. Odigie) | P. Nandwani | 08/13/2026 |
| A13 | Refiner feeder re-cable, with IR, continuity and torque records (if A9 requires it) | D. Fenwick / P. Nandwani | 08/13/2026 |
| A14 | Drafts: DEV-001 Rev C on 08/12/2026; PWR-002 Rev D and MCC-001 Rev C on 08/13/2026; CBL-001 Rev C on 08/14/2026 | D. Fenwick | 08/14/2026 |
| A15 | Checks: DEV-001 on 08/13/2026; PWR-002, MCC-001 and CBL-001 on 08/14/2026 | R. James | 08/14/2026 |
| A16 | Annotate the RFI-014 record to explain the ISO-2030 (07/04/2026) date | R. James | 08/14/2026 |
| A17 | Issue a current RFI register to D. Okonkwo; responders close the other open Line 2 RFIs | C. Whitmore / named responders | 08/14/2026 |
| A18 | Agree with S. Beaufort that BV-2026-L2-01 covers what Criterion 1 requires (see 1.12) | R. James | 08/14/2026 |
| A19 | Escalate to G. Sutcliffe the same day if any of A1–A17 is not complete (restart criteria §7) | R. James | 08/14/2026 |
| A20 | Issue the four re-issues; stamp and move the superseded issues; notify distribution; close RFI-014 action 4 with the close-out note | D. Okonkwo | 08/17/2026 |

After that: records pack assembly on 08/18–08/19/2026 (D. Okonkwo, C. Whitmore); walk-through with S. Beaufort and the Harrowgate pack to I. Wachowski on 08/20/2026; verifier sign-off on 08/21/2026.

## 1.12  Pack scope

BV-2026-L2-01 is scoped to “Line 2 refiner VFD and associated Section C feeder”. Its list of documents relied upon names PWR-002 and DEV-001, but not MCC-001 or CBL-001. Criterion 1, however, requires the verification pack to cover the Line 2 MCC installation, drive cubicles, motor circuits, EMC provisions and the as-built configuration. The record set therefore covers the whole of Line 2 whatever the pack scope. R. James is to agree the scope with S. Beaufort by 08/14/2026, so that her sign-off can meet Criterion 1 (A18).

# 2  Covering note to Denise Okonkwo

| To | Denise Okonkwo, Engineering Records / Document Control |
| --- | --- |
| From | Red James, Lead Electrical Engineer |
| Copy | Dougie Fenwick; Callan Whitmore |
| Date | 08/07/2026 |
| Subject | Line 2 drawing set for Simone Beaufort's pack (BV-2026-L2-01) — settled |

Denise,

The drawing set for Simone's pack is settled. None of the five documents now in Engineering/Drawings goes in on its current issue. Dougie is re-issuing all four controlled drawings as AS-BUILT, and I will have checked them by close of 08/14/2026. That lets you issue them on 08/17/2026 and start pre-verifier prep on 08/18/2026 with a settled set. Section 1 gives the drawing-by-drawing reasons, and the file note at section 3 records the basis.

The record set. It goes to Simone, and the same set goes into Idris Wachowski's inspection pack, which is due to him by 08/20/2026.

1.	MPP-L2-PWR-002 Rev D — Line 2 Power Distribution Schematic (incorporates RFI-014).

2.	MPP-L2-MCC-001 Rev C — Line 2 MCC General Arrangement.

3.	MPP-L2-CBL-001 Rev C — Line 2 Cable Schedule.

4.	MPP-L2-DEV-001 Rev C — Line 2 MCC Device List.

5.	The Line 2 RFI register, current to 08/14/2026, with written dispositions for:
• RFI-014, -015, -017, -021, -022, -025, -029 and -031;
• the new reconciliation and refiner-feeder RFIs.

6.	The signed walk-down sheets of 08/10–08/11/2026, which are the evidence for the reconciliation RFI.

7.	The change record, for traceability only: RFI-014, with PWR-002 Rev C and Priya's 07/09/2026 markup, both stamped SUPERSEDED.

What I need from you

By 08/10/2026: send Dougie the written dispositions of RFI-017, RFI-021 and RFI-029 from your records. The register says downstream drawing updates are tracked by you, and I need to know whether any of the three changed a drawing.

By 08/10/2026: tell me what was issued as MPP-L2-MCC-001 Rev B, and when. PWR-002 Rev C (06/26/2026), RFI-002 (06/04/2026) and the archived MCC-000 schedule (06/01/2026) all cite GA Rev B, but the GA's own history puts Rev B at 07/08/2026. If there was an earlier Rev B, tell me where its prints are so they can be withdrawn and stamped. The re-issue takes Rev C either way.

By 08/14/2026: get a current RFI register from Callan. The copy in Engineering/RFIs is dated 07/14/2026 and shows eleven items open or pending. Criterion 3 needs every open Line 2 RFI closed before Simone's visit, not only the ones that touch drawings. Two of them are yours: RFI-023 (handover pack contents) and RFI-032 (snagging process).

On 08/17/2026:
• issue the four re-issues through the register;
• stamp the old issues SUPERSEDED and move them to the superseded register;
• notify the distribution lists;
• close RFI-014 action 4 against Rev D, with a note that Rev D was prepared from the walk-down, not from the 07/09/2026 markup, and that the markup's base and its “Bussmann-style” fuse description are superseded.

What does not go in

PWR-002 Rev C on its own, or the 07/09/2026 markup as the record of the installed condition. The markup is not on a true print of Rev C: it shows a different incomer and puts the press, sander and conveyor on the wrong sections.

MCC-001, CBL-001 or DEV-001 at Rev B. DEV-001 Rev B is labelled “issued for verification pack”, but it does not list every installed Section C device and would not pass Simone's Item 2.

MPP-L2-MCC-000 Rev G (the superseded pre-upgrade schedule), or the removed-cable specification CBL-UNSCR-L2.

Anything showing a refiner motor replacement or a sander cable re-pull. Neither is an approved change.

If something is late: if a re-issue has not reached you, checked, by 08/17/2026, do not fill the gap with the old issue or the markup. I will have escalated to Grainne on 08/14/2026 under §7 of the restart criteria, and I will give you the instruction in writing.

I am also raising one point with Simone. BV-2026-L2-01 is scoped to the refiner VFD and its Section C feeder, but Criterion 1 needs the whole Line 2 MCC, drive cubicles, motor circuits and EMC provisions. The record set covers all of Line 2 regardless.

Outside the drawing set. You will meet these at pack assembly. They sit with their owners, and this note does not settle them:

Drive Parameter Record (Fiona): last updated 07/02/2026. The refiner row holds 30 kW / 58 A, which are the factory-template values, and the drive still held them on 08/06/2026. Criterion 3 fails any row still holding template values.

IR test record (Priya): IR-L2-SND-04 is still a FAIL. The re-test is due 08/11/2026.

Isolation log (Marcus / Callum): the copy runs only to 07/15/2026. ISO-2041 is open with its DC-bus discharge entries “NOT RECORDED”, and PTW-L2-0087 is not closed out.

Commissioning checklist (Callan): items 3–8, 10 and 12–20 were open at the last update.

Red

# 3  File note — basis settled

| Subject | Line 2 controlled record set for pre-energisation verification (BV-2026-L2-01) and the Harrowgate inspection — basis settled |
| --- | --- |
| Project | PROJ-L2VFD-2026 — Line 2 MCC VFD Upgrade |
| Date | 08/07/2026 |
| Recorded by | R. James, Lead Electrical Engineer |
| Copy | D. Okonkwo (Document Control); D. Fenwick (drawing re-issue queue) |

### Basis

1.	One record set. The drawings sent to Document Control for BV-2026-L2-01 are the controlled record of Line 2 as installed, and the same set goes to the Harrowgate inspection pack. The test is Restart Criterion 3, read with QMS-STD-ENG-001 Rev D §4 and §5. The Line 2 RFI register is what each drawing answers to.

2.	Four AS-BUILT re-issues. The four controlled drawings are re-issued at their next unused revision letters: MPP-L2-PWR-002 Rev D, MPP-L2-MCC-001 Rev C, MPP-L2-CBL-001 Rev C and MPP-L2-DEV-001 Rev C. D. Fenwick prepares them, R. James checks them by 08/14/2026, and Document Control issues them on 08/17/2026. Each revision note cites the RFIs it incorporates, and superseded issues are stamped and moved to the superseded register.

3.	The markup is retired. The field markup of 07/09/2026 goes to the change record, with superseded PWR-002 Rev C and RFI-014. It is not presented as the record of the installed condition.

4.	Every change traces to an approved RFI. Departures found at the 08/10–08/11/2026 walk-down that no RFI covers go on one itemised reconciliation RFI, approved before drafting. A physical change — the refiner feeder re-cable, if confirmed — has its own RFI.

5.	No drawing is checked with an open RFI against it. RFI-022, RFI-025 and RFI-031 are closed in writing by 08/12/2026.

6.	Where the drawing is right, the field is corrected. VFD motor-cable screens are re-terminated 360° at both ends (IEC 61800-3; DTX-IOM-2025-04 §3.2) by 08/13/2026. No drawing records single-end bonding.

7.	Changes that are not approved are not drawn. The refiner motor replacement and the sander cable re-pull stay outside the set until each has an approved RFI.

8.	Escalation. If any re-issue is not checked by close of 08/14/2026, or any condition in items 4–6 is not met by then, R. James escalates to the Plant Manager the same day under §7 of the restart criteria. The set is not completed with an unchecked drawing, an uncorrected markup, or a drawing carrying an open RFI.

### Grounds

None of the five documents matches the installed condition. Eleven drives are installed, but the GA and device list show four, the schematic five, and the cable schedule six (not the same six). No RFI covers the difference. Sources: IR test record (07/25/2026); Drive Parameter Record; isolation log ISO-2040 and ISO-2043.

The 07/09/2026 markup is not on a true print of PWR-002 Rev C: the incomer differs, and the press, sander and conveyor are on the wrong sections. It describes the fitted BFW-80aR fuse as “Bussmann-style”, and it is unchecked.

CBL-001 Rev B states that its rows other than RFI-014's are unverified, and it omits the RFI-014 fuse reference. On its own figures the refiner feeder fails the site derating rule: 64.7 A tabulated capacity is required, and 6 mm² is rated 49 A.

DEV-001 Rev B would not pass Item 2 of BV-2026-L2-01, which checks the device list against the devices installed in Section C.

MCC-001 “Rev B” is cited by documents dated before the GA's own 07/08/2026 Rev B issue.

RFI-025 is open and the field departs from the drawings. RFI-022 and RFI-031 are pending with the vendor.

Harrowgate's booking of 07/09/2026 asks for the latest controlled schematic matching the as-built configuration.

### Responsibilities

| Who | Holds |
| --- | --- |
| R. James | • RFI-025 closed by 08/10/2026; RFI-022 and RFI-031 by 08/12/2026. • Refiner feeder decision by 08/11/2026; reconciliation RFI approved by 08/12/2026. • Checks on 08/13–08/14/2026; RFI-014 record annotated. • Pack scope agreed with S. Beaufort; escalation on 08/14/2026. |
| D. Fenwick | • MCC walk-down and refiner feeder calculation. • Reconciliation (and, if needed, re-cable) RFIs raised. • Four re-issues drafted 08/12–08/14/2026. |
| P. Nandwani | • Cable walk-down; sander re-test per DTX-IOM-2025-04 §6.1. • Screen re-termination and checklist item 3 by 08/13/2026. |
| D. Okonkwo | • Dispositions of RFI-017, -021 and -029, and the MCC-001 Rev B history, by 08/10/2026. • Issue, supersede and notify on 08/17/2026; RFI-014 action 4 closed. |
| C. Whitmore | • DriveTec written responses to RFI-022 and RFI-031 by 08/11/2026. • Current RFI register to Document Control by 08/14/2026. |

Also recorded. BV-2026-L2-01 is scoped to the refiner VFD and its Section C feeder. Criterion 1 covers the Line 2 MCC installation, drive cubicles, motor circuits and EMC provisions. The record set covers the whole of Line 2, and R. James is to agree the pack scope with S. Beaufort by 08/14/2026.

Records referenced.
• Criteria and standards: MPP-RC-L2-001 Rev A; QMS-STD-ENG-001 Rev D; MPP-STD-SUM-05; DTX-DS-2025-06; DTX-IOM-2025-04; IEC 61800-3 extract.
• Drawings and change records: Line 2 RFI register (07/14/2026); RFI-014; MPP-L2-PWR-002 Rev C and field markup (07/09/2026); MPP-L2-MCC-001 Rev B; MPP-L2-CBL-001 Rev B; MPP-L2-DEV-001 Rev B.
• Field and commissioning records: isolation log; IR test record (07/25/2026); Drive Parameter Record; termination notes (07/11/2026); refiner drive export (08/06/2026).
• Gate and project documents: BV-2026-L2-01; Harrowgate booking (07/09/2026); project plan Rev B (risk R2).

Signed: ______   R. James, Lead Electrical Engineer        Date: 08/07/2026